Numbers of LMB Channels Required for ATLAS Pixel Detector Cooling System

This is considered independent of sensors on silicon detector modules themselves.

Pixel Barrel:

B-physics layer: 9 circuits of 2 staves in series: 9 inputs, 9 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1 per E-LMB analog input channel)

(1)	Input, stave tube 1

(2)	Output, stave tube 1 or Input, stave tube 2

(3)	Output, stave tube 2	exhaust (control function)

(4)	Output, stave tube 2 exhaust (reserve sensor for control function)

(5)	Exhaust Remote (control function)

(6)	Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		54 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		9

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		9

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		9

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		9

Barrel Layer 1: 21 circuits of 2 staves in series: 21 inputs, 21 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1)	Input, stave tube 1

(2)	Output, stave tube 1 or Input, stave tube 2

(3)	Output, stave tube 2	exhaust (control function)

(4)	Output, stave tube 2 exhaust (reserve sensor for control function)

(5)	Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		126 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		21

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		21

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		21

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		21

Barrel layer 2: 28 circuits of 2 staves in series: 28 inputs, 28 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1)	Input, stave tube 1

(2)	Output, stave tube 1 or Input, stave tube 2

(3)	Output, stave tube 2	exhaust (control function)

(4)	Output, stave tube 2 exhaust (reserve sensor for control function)

(5)	Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		168 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		28

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		28

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		28

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		28

Pixel Disks:

10 disks of 12 sectors each: pairs of sectors on each circuit. (60 circuits)

Sensors (NTC) on or near on-detector structure per circuit

(1)	Input, stave tube 1

(2)	Output, stave tube 1 or Input, stave tube 2

(3)	Output, stave tube 2	exhaust (control function)

(4)	Output, stave tube 2 exhaust (reserve sensor for control function)

(5)	Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		360 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		60

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		60

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		60

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		60

Numbers of LMB Channels Required for ATLAS SCT Detector Cooling System

This is considered independent of sensors on silicon detector modules themselves.

SCT Barrel:

Layer 3 : 8  4-fold circuits of 2 +2 staves in series/parallel 16 inputs, 8 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1 per E-LMB analog input channel)

- Input, stave tube 1,1

- Input, stave tube 2,1

- Output, stave tube 1,1 or Input, stave tube 1,2

- Output, stave tube 2,1 or Input, stave tube 2,2

- Output, stave tube 1,2 exhaust (control function)

- Output, stave tube 1,2 exhaust (reserve sensor for control function)

- Output, stave tube 2,2 exhaust (control function)

- Output, stave tube 2,2 exhaust (reserve sensor for control function)

- Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		80 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		16

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		8

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		16

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		8

Layer 4 : 10  4-fold circuits of 2 +2 staves in series/parallel 20 inputs, 10 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1 per E-LMB analog input channel)

- Input, stave tube 1,1

- Input, stave tube 2,1

- Output, stave tube 1,1 or Input, stave tube 1,2

- Output, stave tube 2,1 or Input, stave tube 2,2

- Output, stave tube 1,2 exhaust (control function)

- Output, stave tube 1,2 exhaust (reserve sensor for control function)

- Output, stave tube 2,2 exhaust (control function)

- Output, stave tube 2,2 exhaust (reserve sensor for control function)

- Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		100 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		20

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		10

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		20

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		10

Layer 5 : 12  4-fold circuits of 2 +2 staves in series/parallel 24 inputs, 12 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1 per E-LMB analog input channel)

- Input, stave tube 1,1

- Input, stave tube 2,1

- Output, stave tube 1,1 or Input, stave tube 1,2

- Output, stave tube 2,1 or Input, stave tube 2,2

- Output, stave tube 1,2 exhaust (control function)

- Output, stave tube 1,2 exhaust (reserve sensor for control function)

- Output, stave tube 2,2 exhaust (control function)

- Output, stave tube 2,2 exhaust (reserve sensor for control function)

- Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		120 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		24

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		12

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		24

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		12

Layer 6 : 14  4-fold circuits of 2 +2 staves in series/parallel 28 inputs, 14 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1 per E-LMB analog input channel)

- Input, stave tube 1,1

- Input, stave tube 2,1

- Output, stave tube 1,1 or Input, stave tube 1,2

- Output, stave tube 2,1 or Input, stave tube 2,2

- Output, stave tube 1,2 exhaust (control function)

- Output, stave tube 1,2 exhaust (reserve sensor for control function)

- Output, stave tube 2,2 exhaust (control function)

- Output, stave tube 2,2 exhaust (reserve sensor for control function)

- Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		140 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		28

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		14

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		28

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		14

18 disks of 4 quadrants each:

14 disks with 3-fold circuits on quadrants (3 inputs, 1 output)

168 inputs, 56 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1 per E-LMB analog input channel)

PER QUADRANT

- Input, circuit tube 1

- Input, circuit tube 2

- Input, circuit tube 3

- Output, circuit tube 1 exhaust (control function)

- Output, circuit tube 1 exhaust (reserve sensor for control function)

- Output, circuit tube 2 exhaust (control function)

- Output, circuit tube 2 exhaust (reserve sensor for control function)

- Output, circuit tube 3 exhaust (control function)

- Output, circuit tube 3 exhaust (reserve sensor for control function)

- Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		616 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		168

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		56

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		168

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		56

4 disks with single circuits on quadrants (1 input, 1 output)

16 inputs, 16 outputs

Sensors (NTC) on or near on-detector structure per circuit

(1 per E-LMB analog input channel)

PER QUADRANT

- Input, circuit tube 1

- Output, circuit tube 1 exhaust (control function)

- Output, circuit tube 1 exhaust (reserve sensor for control function)

- Exhaust Remote (control function)

- Exhaust Remote (reserve sensor for control function)

SUBTOTAL:		80 NTC sensors

PIDs in LMB controllers for flow control:

(1 per E-LMB analog output channel)		16

PIDs in LMB controllers for boiling pressure control (OPTIONAL)

(1 per E-LMB analog output channel)		16

Pressure measurement (upstream of capillary)

(1 per E-LMB analog input channel)		16

Pressure measurement (exhaust)

(1 per E-LMB analog input channel)		16

#### TUBE BUNDLES

The assumption made is that each tube bundle has active insulation over the ~30 metres between PPB3 and PPB1 which is divided into 5 zones as follows :

(1) PPB1 to end of ID volume

(2) End of ID volume to PPB2

(3) PPB2 : PPB3 in 3 stages

Each zone of each bundle is assumed to have four temperature sensors : two for monitoring and two for control purposes. These require PID activity to control the active insulation heaters.

Service Bundle inventory

Layer			Cooled Supply/end		Exhaust /end 		 Totals

Pixel B layer			4(3 tubes)		4(3 tubes)		8 (3 tubes)

Pixel layers 1,2		8(3 tubes)		8(3 tubes)		16 (3 tubes)

Pixel disks			4(4 tubes)		4(4 tubes)		8 (4 tubes)					4(3 tubes)		4(3 tubes)		8 (3 tubes)

SCT layers 3-6		2(11 tubes)		2(5 tubes)		4 (11,5 tubes)

2(11 tubes)		2(6 tubes)		4 (11,6 tubes)

SCT Disks			4(11 tubes)		4(5 tubes)		8 (11,5 tubes)

4(11 tubes)		4(4 tubes)		8 (11,4 tubes)

Total No bundles : 64

No Zones (64*5) : 320

# No Sensors (64*5*4) : 1280

No PID controllers (64*5) : 320

##### Immediate requirements (Oct 00 (early 2001)

##### for E-LMBs and DAC add-ons (from NIKHEF)

###### Evaporative Cooling Demonstrator Requirement

(A prototype circulator/E-LMB-based DAQ

System for SCT assembly site 1 [Oxford, mid 2001])

Phase (2) Requirement			Analog In	E-LMBs 	E-LMB DACs

SCT 4-folds			=  	174		3

Pixel staves (16* 6 sensors) 	=	96		1.5

SCT Circuits	(6 * 10)	= 	60		1

Pixel circuits   (8 * 6) 	=	48		3/4

Tube bundles (assume 6)	=	120		2

Pressures (SCT)		=	18		1/4

PIDs (SCT)			=	18				4.5

Pressures (pixels)		=	16		1/4

PIDs (pixels)			=	16				4

Other structures		=	128		2

TOTALs			11		8.5+

+  Assumes 4 DAC add-ons, developed by NIKHEF, can be supported from one E-LMB mother-board. DAC added-on E-LMBs are subset of total E-LMB requirement.

PVSS2 Development licenses :

- October 2000 for CERN lab (Paer Hammarstedt)

- CPP Marseille (early 2001) (Greg Hallewell)

- Wuppertal (Kersten, October 2000)

##### Possible Oxford SCT layer 6 Requirement

(NOT OFFICIAL : NOT CHECKED WITH

SCT COMMUNITY (Brenner/Wastie):

BUT POSSIBLY REALISTIC)

Assumption : Oxford need E-LMBs to test SCT layer 6 (r=60 cm) mid 2001, and that

SCT modules (12*4*14)  	= 	672		10.5

Circuit Sensors (10*14)	= 	140		2.25

Pressures (SCT)		=	42		0.75

PIDs	(SCT)			=	42				10.5+

TOTALS			13.5		10.5

+  Assumes 4 DAC add-ons, developed by NIKHEF, can be supported from one E-LMB

mother-board. DAC added-on E-LMBs are subset of total E-LMB requirement.

PVSS2 Development licenses :

- October 2000 (needs input from Roy Wastie/Oxford)