| Draft |
| --- |
| ATLAS COOLING OF THE DETECTOR TEST IN MAGNETIC fIELD |
| Objectives To validate material in UX cavern Abstract Test of an ultrasonic level transmitter transmitter in a magnetic field. Click here to access to the guidelines |
| Prepared | Verified | Approved |
| By: | BONNEAU Pierre | By: | Reviewer | By: | Approver |
| Date: | 2002/11/05 | Date: | 200Y/MM/DD | Date: | 200Y/MM/DD |
| Distribution List |
| History of Changes |
| Rev. No. | Date | Pages | Description of Changes |

Table of contents

1.	Description	3

2.	Results	4

2.1	Transmitter in horizontal position	4

2.2	Transmitter in vertical position	4

3.	conclusion	5

# Description

We have tested an ultrasonic level transmitter in a magnetic field. The transmitter is a BURKERT type 8175, measuring range from 0.3 to 10 m, output 4-20mA, (Figure 1). Exact serial number is 430822M and detailed technical characteristics are in annex: 8175_Product.pdf .

Figure 1 – BURKERT Ultrasonic Level Transmitter Type 8175

The transmitter is connected with a 5m shielding cable to a Labview DAQ system (Figure 2).

We install the transmitter in horizontal and vertical position inside the magnet MNP17 in the building 168 – Thanks to R. Rey-Mermier and Felix Bergsma of EP-TA3. This magnet allows field from 0 to 2700 [Gauss] with presetting steps of 85, 171, 342, 684, 1350 and 2700 [Gauss].

Figure 2 – Layout of the test

# Results

## Transmitter in horizontal position

We don’t see any effect of the magnetic field on the transmitter – see Figure 3. The sensor was turned horizontally by 90° and no change was observed. No effect on the LCD display.

Figure 3

## Transmitter in vertical position

We can observe an erratic signal when 86[Gauss] are applied and the signal goes out of range starting from 171[Gauss]. When the magnet is stopped the sensor returns to its original value – See figure 4.

Figure 4

# conclusion

The function of the water level transmitter is very important in the Leakless cooling systems, as it should detect small variation of the liquid in the tank to prevent leak in the overpressure part of the circuit. As any detected variation will send alarm and stop the system the sensor has to be reliable and steady.

The ultrason technology is an interesting solution as we have an appropriate accuracy for a moderate price.

The magnetic field in the cavern UX15 is expected to be around 300[Gauss] at the location of the cooling stations with no indication on the direction.

We see with this test that we have to take care of this problem.

Discussions are on going with the manufacturer to understand the effect of the magnetic field on the sensor and to try to limit it.