C6F14  - PIPING

|  | Rad Hard | Compatibility | Gas Permeability Px1010(cm3mm/cm2 s cm Hg) (DATA: Angst+Pfister) | GLOBAL RESULT |
| --- | --- | --- | --- | --- |
| SS | OK | OK | 0 | OK |
| Aluminum | OK | OK (if fluid is pure) Not well know if fluid is contaminated with H2O, O2, C-H due to F-production | 0 | OK? |
| PEEK | 108 rad (Data: TIS-CFM/MTR/96-17) | OK (Data: 3M) |  | OK |
| PUR | 107 rad (Data: Angst+Pfister) | OK (Data: 3M) | 5 N2 15-50 O2 140-400 CO2 | OK |
| Polypropylene PP | 107 rad (Data: Angst+Pfister) |  | 3-5 N2 ~10 O2 ~ 35 CO2 | ? |
| Polyethylene PE | 108 rad (Data: CERN 82-10) | OK (Data: DELPHI 95-21 RICH 66) | 0.1 N2 ~ 1 O2 1-6 CO2 8 H2 | OK |
| Nylon (Polyamide 6) | 107 rad (Data: CERN 82-10) | OK (Data: 3M) | ~ 2 N2 ~ 1 O2 1-6 CO2 8 H2 | OK |
| Rilsan (polyamide 11) |  | OK (Data: 3M) Discolaration, Weight loss, but mechanical prop. OK (Data: DELPHI 95-21 RICH 66) |  | BAD |
| Teflon (PTFE) | BAD | BAD |  | BAD |
| PVC | 108 rad (Data: Angst+Pfister) | Some effect (Data: 3M) | 0.3 N2 ~ 1 O2 1-10 CO2 33 H2 | BAD |

Note: one should avoid plastics with the fluorocarbons as they take out the plastiziser and the product becomes brittle. Source: G. Lenzem, DELPHI RICH and 3M

# Footnotes

BAD means that material does not show any damage up to the indicated dose. BAD means that it is affected well below 105 rad.

Effect means change of weight and/or volume after > 72h immersion in C6F14. Some effect means > 1%. BAD means >4%.

# Text boxes

See

Note